## results
File name and field name | Abs threshold | Rel threshold | #hours with big ref diff at abs value (out of 8760) | Max rel diff | Abs value at mas ref diff | Notes on error file diff
2ZoneDataCenterHVAC_wEconomizer
WESTDATACENTER_EQUIP:ITE CPU Electric Power [W](Hourly) | 0.1 | 0.005 | 103 | 3.893% | 1190.8051 | Diffs in existing severe error
WESTDATACENTER_EQUIP:ITE Fan Electric Power [W](Hourly) | 0.1 | 0.005 | 119 | 5.591% | 1190.7455 | *************
WESTDATACENTER_EQUIP:ITE UPS Electric Power [W](Hourly) | 0.1 | 0.005 | 111 | 4.59% | 238.1551 | ************* ** Severe ** FindRootSimpleController: Previous controller action error continues for controller = EAST CW COIL CONTROLLER
WESTDATACENTER_EQUIP:ITE UPS Heat Gain to Zone Rate [W](Hourly) | 0.1 | 0.005 | 111 | 4.59% | 238.1551 | - ************* ** ~~~ ** This error occurred 51 total times;
WESTDATACENTER_EQUIP:ITE Total Heat Gain to Zone Rate [W](Hourly) | 0.1 | 0.005 | 111 | 4.59% | 2619.7057 | + ************* ** ~~~ ** This error occurred 63 total times;
WESTDATACENTER_EQUIP:ITE Standard Density Air Volume Flow Rate [m3/s](Hourly) | 0.001 | 0.005 | 119 | 5.393% | 0.40137 | ************* ** ~~~ ** during Warmup 0 times;
WESTDATACENTER_EQUIP:ITE Air Inlet Dry-Bulb Temperature [C](Hourly) | 0.2 | -1 | 51 | 3.893% | 0.64085 | ************* ** ~~~ ** during Sizing 0 times.
WESTDATACENTER_EQUIP:ITE Air Inlet Dewpoint Temperature [C](Hourly) | 0.2 | -1 | 68 | 12124% | 0.20366
WESTDATACENTER_EQUIP:ITE Air Inlet Relative Humidity [%](Hourly) | 0.001 | 0.005 | 111 | 12.03% | 0.0082386
WESTDATACENTER_EQUIP:ITE Air Outlet Dry-Bulb Temperature [C](Hourly) | 0.2 | -1 | 46 | 2.324% | 0.5719
WESTDATACENTER_EQUIP:ITE Supply Heat Index [](Hourly) | 0.001 | 0.005 | 70 | 6.848% | 0.0051175
WEST ZONE:Zone ITE CPU Electric Power [W](Hourly) | 0.1 | 0.005 | 103 | 3.893% | 1190.8051
WEST ZONE:Zone ITE Fan Electric Power [W](Hourly) | 0.1 | 0.005 | 119 | 5.591% | 1190.7455
WEST ZONE:Zone ITE UPS Electric Power [W](Hourly) | 0.1 | 0.005 | 111 | 4.59% | 238.1551
WEST ZONE:Zone ITE UPS Heat Gain to Zone Rate [W](Hourly) | 0.1 | 0.005 | 111 | 4.59% | 238.1551
WEST ZONE:Zone ITE Total Heat Gain to Zone Rate [W](Hourly) | 0.1 | 0.005 | 111 | 4.59% | 2619.7057
EMS:Power Utilization Effectiveness [](Hourly) | 0.001 | 0.005 | 297 | 3.045% | 0.033003
WEST ZONE:Zone Air Temperature [C](Hourly) | 0.2 | -1 | 66 | 3.349% | 0.80313
WEST ZONE:Zone Air Relative Humidity [%](Hourly) | 0.001 | 0.005 | 117 | 10.78% | 0.47334
EAST ZONE CW COOLING COIL:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 199 | 147031% | 178.9774
EAST ZONE CW COOLING COIL:Cooling Coil Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 197 | 147031% | 178.9774
WEST DATA CENTER IEC:Evaporative Cooler Total Stage Effectiveness [](Hourly) | 0.001 | 0.005 | 1 | 1.064% | 0.0033188
EAST DATA CENTER IEC:Evaporative Cooler Operating Mode Status [](Hourly) | 0.001 | 0.005 | 13 | 99900% | 0.016667
WEST DATA CENTER DEC:Evaporative Cooler Stage Effectiveness [](Hourly) | 0.001 | 0.005 | 53 | 99900% | 0.175
WEST DATA CENTER IEC:Evaporative Cooler Electric Power [W](Hourly) | 0.1 | 0.005 | 1 | 1.097% | 4.6434
WEST DATA CENTER IEC:Evaporative Cooler Water Volume [m3](Hourly) | 0.001 | 0.005 | 0 | 0.001949% | 7.9237e-08
CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 297 | 100% | 0.25812
CHILLER:Chiller Evaporator Inlet Temperature [C](Hourly) | 0.2 | -1 | 952 | 34.48% | 2.1755
CHILLER:Chiller Evaporator Outlet Temperature [C](Hourly) | 0.2 | -1 | 952 | 34.48% | 2.1755
CHILLER:Chiller Condenser Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 297 | 100% | 0.29727
CHILLER:Chiller Condenser Inlet Temperature [C](Hourly) | 0.2 | -1 | 193 | 7.729% | 0.71567
CHILLER:Chiller Condenser Outlet Temperature [C](Hourly) | 0.2 | -1 | 193 | 7.729% | 0.71567
WEST ZONE INLET NODE:System Node Temperature [C](Hourly) | 0.2 | -1 | 55 | 3.294% | 0.51541
WEST ZONE INLET NODE:System Node Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 24 | 7.354% | 0.41185
WEST ZONE IEC OUTLET NODE:System Node Setpoint Temperature [C](Hourly) | 0.2 | -1 | 61 | 3.976% | 0.59821
UserDefinedRoomAirPatterns | [5 empty] | Diffs in existing warnings
ZN1_SW_1:W_EXTWALL:2:Surface Inside Face Temperature [C](Hourly) | 0.2 | -1 | 46 | 5.556% | 0.88106 | ************* ** Warning ** CoolingTower:SingleSpeed "CHILLER PLANT CONDENSER" Cooling tower water outlet temperature is below the specified minimum condenser loop temp error continues...
ZN2_S_1:S_EXTWALL:2:Surface Inside Face Temperature [C](Hourly) | 0.2 | -1 | 56 | 6.475% | 0.96939 | - ************* ** ~~~ ** This error occurred 10440 total times;
ZN9_CORE_1:FLOOR:Surface Inside Face Temperature [C](Hourly) | 0.2 | -1 | 17 | 5.073% | 0.79898 | + ************* ** ~~~ ** This error occurred 10582 total times;
ZN9_CORE_1 EXHAUST NODE 1:System Node Temperature [C](Hourly) | 0.2 | -1 | 76 | 15.73% | 2.5045 | ************* ** ~~~ ** during Warmup 0 times;
ZN1_SW_1 RETURN OUTLET:System Node Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 155 | 70% | 0.36167 | ************* ** ~~~ ** during Sizing 0 times.
ZN1_SW_1 RETURN OUTLET:System Node Enthalpy [J/kg](Hourly) | 0.001 | 0.005 | 502 | 6.874% | 1785.9867 | - ************* ** ~~~ ** Max=4.999976 Min=4.381471
+ ************* ** ~~~ ** Max=4.99994 Min=4.381471
GasTurbChillerHeatRecoveryAuto | [5 empty] | Existing warnings
BIG WATER HEATER:Water Heater Tank Temperature [C](Hourly) | 0.2 | -1 | 317 | 9.908% | 4.5135
BIG WATER HEATER:Water Heater Use Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 162 | 20.8% | 9.9538
BIG WATER HEATER:Water Heater Source Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 317 | 56634% | 375.1485
CHILLED WATER LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 91 | 100% | 28.1349
HOT WATER LOOP:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 141 | 20.08% | 11.6815
REHEAT COIL ZONE 1:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 92 | 65.8% | 52.8002
DETAILED COOLING COIL:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 89 | 100% | 28.9618
BIG CHILLER:Chiller Drive Shaft Power [W](Hourly) | 0.1 | 0.005 | 89 | 100% | 7.7622
BIG CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 91 | 100% | 28.1349
BIG CHILLER:Chiller Evaporator Inlet Temperature [C](Hourly) | 0.2 | -1 | 9 | 4.589% | 0.69256
BIG CHILLER:Chiller Evaporator Outlet Temperature [C](Hourly) | 0.2 | -1 | 9 | 18.84% | 1.5485
BIG CHILLER:Chiller Evaporator Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 72 | 100% | 0.00073505
BIG CHILLER:Chiller Condenser Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 90 | 100% | 35.8972
BIG CHILLER:Chiller Condenser Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 4 | 100% | 0.27483
BIG CHILLER:Chiller Lube Recovered Heat Energy [J](Hourly) | 0.001 | 0.005 | 89 | 100% | 3619.0436
BIG CHILLER:Chiller Gas Rate [W](Hourly) | 0.1 | 0.005 | 89 | 100% | 49.372
BIG CHILLER:Chiller Gas Energy [J](Hourly) | 0.001 | 0.005 | 89 | 100% | 177739.252
BIG CHILLER:Chiller Gas Mass [kg](Hourly) | 0.001 | 0.005 | 84 | 100% | 0.004086
BIG CHILLER:Chiller Exhaust Temperature [C](Hourly) | 0.2 | -1 | 4 | 100% | 109.9646
BIG CHILLER:Chiller Heat Recovery Inlet Temperature [C](Hourly) | 0.2 | -1 | 321 | 9.867% | 4.508
BIG CHILLER:Chiller Heat Recovery Outlet Temperature [C](Hourly) | 0.2 | -1 | 321 | 9.832% | 4.5082
ShopWithPVandStorage | [5 empty] | Existing warnings
PV:ZN_1_FLR_1_SEC_1_CEILING:Generator Requested Electric Power [W](Hourly) | 0.1 | 0.005 | 3 | 1.034% | 84.9993
PV:ZN_1_FLR_1_SEC_3_CEILING:Generator Requested Electric Power [W](Hourly) | 0.1 | 0.005 | 3 | 1.034% | 84.9993
PV:ZN_1_FLR_1_SEC_5_CEILING:Generator Requested Electric Power [W](Hourly) | 0.1 | 0.005 | 3 | 1.034% | 84.9993
PV INVERTER:Inverter Thermal Loss Rate [W](Hourly) | 0.1 | 0.005 | 10 | 100% | 200
Whole Building:Facility Total Purchased Electric Power [W](Hourly) | 0.1 | 0.005 | 10 | 2.281% | 133.3333
Whole Building:Facility Total Purchased Electric Energy [J](Hourly) | 0.001 | 0.005 | 10 | 2.281% | 480000.0001
Whole Building:Facility Net Purchased Electric Power [W](Hourly) | 0.1 | 0.005 | 10 | 400% | 1.2127e-12
Whole Building:Facility Net Purchased Electric Energy [J](Hourly) | 0.001 | 0.005 | 10 | 400% | 4.3656e-09
Whole Building:Facility Total HVAC Electric Demand Power [W](Hourly) | 0.1 | 0.005 | 10 | 2.217% | 200
Whole Building:Facility Total Electric Demand Power [W](Hourly) | 0.1 | 0.005 | 10 | 2.022% | 200
MultiSpeedHP_StagedThermostat | [5 empty] | Existing warnings
WEST ZONE:Zone Air System Sensible Heating Energy [J](Hourly) | 0.001 | 0.005 | 113 | 100% | 1034637.3194
WEST ZONE:Zone Air System Sensible Cooling Energy [J](Hourly) | 0.001 | 0.005 | 25 | 99900% | 418186.715
WEST ZONE:Zone Air Temperature [C](Hourly) | 0.2 | -1 | 9 | 2.943% | 0.47284
WEST ZONE:Zone Air Relative Humidity [%](Hourly) | 0.001 | 0.005 | 61 | 2.961% | 0.57756
WEST ZONE:Zone Thermostat Cooling Setpoint Temperature [C](Hourly) | 0.2 | -1 | 7 | 3.183% | 0.75556
WEST ZONE:Zone Thermostat Staged Number [](Hourly) | 0.001 | 0.005 | 8 | 100% | 0.041667
SUPPLY FAN 1:Fan Electric Power [W](Hourly) | 0.1 | 0.005 | 90 | 36.26% | 78.8236
HEAT PUMP DX HEATING COIL 1:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 69 | 30.94% | 1214.2999
HEAT PUMP DX HEATING COIL 1:Heating Coil Heating Energy [J](Hourly) | 0.001 | 0.005 | 69 | 30.94% | 4371479.6518
HEAT PUMP DX HEATING COIL 1:Heating Coil Gas Rate [W](Hourly) | 0.1 | 0.005 | 68 | 31.38% | 685.0555
HEAT PUMP DX HEATING COIL 1:Heating Coil Defrost Gas Rate [W](Hourly) | 0.1 | 0.005 | 46 | 99900% | 6.4814
HEAT PUMP DX HEATING COIL 1:Heating Coil Defrost Gas Energy [J](Hourly) | 0.001 | 0.005 | 55 | 99900% | 23333.2
DXAC HEAT PUMP 1:Unitary System Fan Part Load Ratio [](Hourly) | 0.001 | 0.005 | 66 | 54.95% | 0.35463
DXAC HEAT PUMP 1:Unitary System Compressor Part Load Ratio [](Hourly) | 0.001 | 0.005 | 83 | 560.2% | 0.17491
DXAC HEAT PUMP 1:Unitary System DX Coil Cycling Ratio [](Hourly) | 0.001 | 0.005 | 75 | 54.95% | 0.35463
DXAC HEAT PUMP 1:Unitary System DX Coil Speed Ratio [](Hourly) | 0.001 | 0.005 | 95 | 381.6% | 0.12646
DXAC HEAT PUMP 1:Unitary System DX Coil Speed Level [](Hourly) | 0.001 | 0.005 | 75 | 56.98% | 0.72593
DXAC HEAT PUMP 1:Unitary System Total Heating Rate [W](Hourly) | 0.1 | 0.005 | 99 | 100% | 888.9051
MIXED AIR NODE:System Node Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 89 | 36.26% | 0.21627
ElectricEIRChillerHeatRecoveryAuto | [5 empty] | Existing warnings
CHILLED WATER LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.5463% | 51.7189
HOT WATER LOOP:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 1 | 1.548% | 59.0774
REHEAT COIL ZONE 1:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 5.839% | 16.4805
DETAILED COOLING COIL:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.5453% | 51.3936
BIG CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.5463% | 51.7189
BIG CHILLER:Chiller Evaporator Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 1 | 0.6894% | 0.0013043
HeatPumpWaterHeaterStratified | [5 empty] | Existing warnings
SPACE1-1 ZONE COIL:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 2 | 2.457% | 0.090496
HPWHDXCOIL:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 2.504% | 2.5605
HPWHTANK:Water Heater Source Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 1 | 2.508% | 4.021
HPWHDXCOIL:Cooling Coil Total Water Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 2.508% | 4.2326
HPWHDXCOIL:Cooling Coil Water Heating Electric Power [W](Hourly) | 0.1 | 0.005 | 1 | 1.968% | 1.5238
ZONE5HEATPUMPWATERHEATER:Water Heater Compressor Part Load Ratio [](Hourly) | 0.001 | 0.005 | 1 | 2.524% | 0.0013396
HospitalLowEnergy | [5 empty] | Diffs in existing warnings
FLOOR 2 LAB 1:Zone Air Relative Humidity [%](Hourly) | 0.001 | 0.005 | 132 | 12.9% | 6.0754 | ************* ** Warning ** CoolingTower:VariableSpeed "CONDENSERLOOP CHILLER TOWERSYS COOLTOWER" - Tower approach temperature is out of range error continues...
FLOOR 2 IMAGING 2 VAV BOX COMPONENT:Zone Air Terminal Outdoor Air Volume Flow Rate [m3/s](Hourly) | 0.001 | 0.005 | 1 | 0.7495% | 0.0010026 | - ************* ** ~~~ ** This error occurred 38032 total times;
FLOOR 1 CAFE HEAT PUMP INLET NODE:System Node Standard Density Volume Flow Rate [m3/s](Hourly) | 0.001 | 0.005 | 142 | 99900% | 0.00047165 | + ************* ** ~~~ ** This error occurred 38078 total times;
5ZoneCoolBeam
SPACE3-1:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.7397% | 3.6156 | None
SPACE5-1:Zone Predicted Sensible Load to Cooling Setpoint Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.6917% | 15.0724
CENTRAL CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 15 | 3.125% | 419.4451
VSHeatPumpWaterHeater | [5 empty] | Existing severe error (happens in the non-cache version as well)
HPWHDXCOILVS:Cooling Coil Water Heating Electric Power [W](Hourly) | 0.1 | 0.005 | 154 | 99900% | 0.59233 | Severe ** FindRootSimpleController: Controller error for controller = "CENTRAL COOLING COIL CONTOLLER 1"
HPWHDXCOILVS:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 165 | 99900% | 1.4838 | ** ~~~ ** Environment=JAN14, at Simulation time=12/16 04:45 - 05:00
HPWHDXCOILVS:Cooling Coil Total Water Heating Rate [W](Hourly) | 0.1 | 0.005 | 147 | 99900% | 1.966 | ** ~~~ ** Controller function is inconsistent with user specified controller action = Reverse action
HPWHFAN:Fan Electric Power [W](Hourly) | 0.1 | 0.005 | 112 | 99900% | 0.020549 | ** ~~~ ** Actuator will be set to maximum action
HPWHTANK:Water Heater Tank Temperature [C](Hourly) | 0.2 | -1 | 124 | 2.556% | 1.493 | ** ~~~ ** Controller control type=Temperature and humidity ratio
HPWHTANK:Water Heater Use Side Outlet Temperature [C](Hourly) | 0.2 | -1 | 124 | 2.556% | 1.493 | ** ~~~ ** Controller temperature setpoint = 6.52E-003 [C]
HPWHTANK:Water Heater Use Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 32 | 2.333% | 49.0604 | ** ~~~ ** Controller sensed temperature = 6.73E-003 [C]
HPWHTANK:Water Heater Source Side Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 109 | 99900% | 0.00040265 | ** ~~~ ** Controller humidity ratio setpoint = 6.52E-003 [kg-H2O/kg-air]
HPWHTANK:Water Heater Source Side Inlet Temperature [C](Hourly) | 0.2 | -1 | 173 | 4.068% | 2.4154 | ** ~~~ ** Controller sensed humidity ratio = 6.73E-003 [kg-H2O/kg-air]
HPWHTANK:Water Heater Source Side Outlet Temperature [C](Hourly) | 0.2 | -1 | 124 | 2.556% | 1.493 | ** ~~~ ** Controller actuator mass flow rate set to 1.63 [kg/s]
HPWHTANK:Water Heater Source Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 147 | 99900% | 1.87
ZONE5HEATPUMPWATERHEATER:Water Heater Compressor Part Load Ratio [](Hourly) | 0.001 | 0.005 | 152 | 99900% | 0.0058268
ZONE5HEATPUMPWATERHEATER:Water Heater Off Cycle Ancillary Electric Power [W](Hourly) | 0.1 | 0.005 | 104 | 99900% | 1.25
ZONE5HEATPUMPWATERHEATER:Water Heater On Cycle Ancillary Electric Power [W](Hourly) | 0.1 | 0.005 | 122 | 99900% | 0.087402
SCHEDULEDELECTRICTANK:Water Heater Electric Power [W](Hourly) | 0.1 | 0.005 | 13 | 51.99% | 2.3131
SPACE1-1 ZONE COIL:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 42 | 128.8% | 2.8128
CoolingTower_VariableSpeed_IdealCondEntTempSetpoint | [5 empty] | Diffs in existing warnings
SPACE2-1:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.6832% | 0.43757 | - ** Warning ** CoolingTower:VariableSpeed "CENTRAL TOWER" - Tower approach temperature is outside model boundaries at 0.84.
CONDENSER TOWER OUTLET NODE:System Node Setpoint Temperature [C](Hourly) | 0.2 | -1 | 72 | 17.89% | 3.9 | - ** ~~~ ** ...Valid range = 1.11 to 40.00. Occurrence info = RUN PERIOD 1, 06/07 16:30 - 16:45
- ** ~~~ ** ...Tower approach temperature passed to the model = 0.83623
+ ** Warning ** CoolingTower:VariableSpeed "CENTRAL TOWER" - Tower approach temperature is outside model boundaries at -3.07.
+ ** ~~~ ** ...Valid range = 1.11 to 40.00. Occurrence info = RUN PERIOD 1, 06/07 16:15 - 16:30
+ ** ~~~ ** ...Tower approach temperature passed to the model = -3.07264
** ~~~ ** ...Approach temperatures outside model boundaries may not adversely affect tower performance.
CentralChillerHeaterSystem_Simultaneous_Cooling_Heating | [5 empty] | Existing warnings
VERTICAL GROUND HEAT EXCHANGER:Ground Heat Exchanger Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 80 | 99900% | 11469.3491
VERTICAL GROUND HEAT EXCHANGER:Ground Heat Exchanger Inlet Temperature [C](Hourly) | 0.2 | -1 | 4469 | 59.5% | 14.2495
VERTICAL GROUND HEAT EXCHANGER:Ground Heat Exchanger Outlet Temperature [C](Hourly) | 0.2 | -1 | 4472 | 72.65% | 9.543
VERTICAL GROUND HEAT EXCHANGER:Ground Heat Exchanger Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 38 | 99900% | 0.15623
CHILLED WATER LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 29 | 25.97% | 3670.4812
CHILLED WATER LOOP:Plant Supply Side Unmet Demand Rate [W](Hourly) | 0.1 | 0.005 | 57 | 99900% | 314.4194
HOT WATER LOOP:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 438 | 99900% | 802.3388
CHILLERBANK:Chiller Heater System Cooling Electric Energy [J](Hourly) | 0.001 | 0.005 | 39 | 102% | 9653283.1331
CHILLERBANK:Chiller Heater System Heating Electric Energy [J](Hourly) | 0.001 | 0.005 | 40 | 99900% | 6953595.5795
CHILLERBANK:Chiller Heater System Cooling Electric Power [W](Hourly) | 0.1 | 0.005 | 39 | 102% | 2681.4675
CHILLERBANK:Chiller Heater System Heating Electric Power [W](Hourly) | 0.1 | 0.005 | 40 | 99900% | 1931.5543
CHILLERBANK:Chiller Heater System Cooling Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 41 | 46.41% | 0.49886
CHILLERBANK:Chiller Heater System Heating Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 12 | 99900% | 0.9374
CHILLERBANK:Chiller Heater System Source Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 31 | 99900% | 0.078117
CHILLERBANK:Chiller Heater System Cooling Inlet Temperature [C](Hourly) | 0.2 | -1 | 19 | 37.5% | 4.3406
CHILLERBANK:Chiller Heater System Heating Inlet Temperature [C](Hourly) | 0.2 | -1 | 1678 | 9.028% | 4.8172
CHILLERBANK:Chiller Heater System Source Inlet Temperature [C](Hourly) | 0.2 | -1 | 4156 | 168.4% | 15.0637
CHILLERBANK:Chiller Heater System Cooling Outlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 4.627% | 0.27191
CHILLERBANK:Chiller Heater System Heating Outlet Temperature [C](Hourly) | 0.2 | -1 | 1707 | 9.028% | 4.8172
CHILLERBANK:Chiller Heater System Source Outlet Temperature [C](Hourly) | 0.2 | -1 | 4450 | 168.4% | 15.0637
CHILLERHEATERMODULE:Chiller Heater Operation Mode Unit 1 [](Hourly) | 0.001 | 0.005 | 9 | 99900% | 0.16667
CHILLERHEATERMODULE:Chiller Heater Part Load Ratio Unit 1 [](Hourly) | 0.001 | 0.005 | 32 | 99900% | 0.083333
CHILLERHEATERMODULE:Chiller Heater Cycling Ratio Unit 1 [](Hourly) | 0.001 | 0.005 | 6 | 99900% | 0.083333
CHILLERHEATERMODULE:Chiller Heater Cooling Electric Power Unit 1 [W](Hourly) | 0.1 | 0.005 | 30 | 100% | 2653.8372
CHILLERHEATERMODULE:Chiller Heater Heating Electric Power Unit 1 [W](Hourly) | 0.1 | 0.005 | 31 | 99900% | 965.7772
CHILLERHEATERMODULE:Chiller Heater Cooling Rate Unit 1 [W](Hourly) | 0.1 | 0.005 | 26 | 99900% | 758.2444
CHILLERHEATERMODULE:Chiller Heater Evaporator Inlet Temperature Unit 1 [C](Hourly) | 0.2 | -1 | 29 | 37.51% | 4.3413
CHILLERHEATERMODULE:Chiller Heater Evaporator Outlet Temperature Unit 1 [C](Hourly) | 0.2 | -1 | 18 | 25.36% | 3.5887
CHILLERHEATERMODULE:Chiller Heater Evaporator Mass Flow Rate Unit 1 [kg/s](Hourly) | 0.001 | 0.005 | 33 | 99900% | 0.044746
CHILLERHEATERMODULE:Chiller Heater Condenser Heat Transfer Rate Unit 1 [W](Hourly) | 0.1 | 0.005 | 441 | 99900% | 452.8903
CHILLERHEATERMODULE:Chiller Heater Capacity Temperature Modifier Multiplier Unit 1 [](Hourly) | 0.001 | 0.005 | 16 | 99900% | 0.081972
CHILLERHEATERMODULE:Chiller Heater EIR Temperature Modifier Multiplier Unit 1 [](Hourly) | 0.001 | 0.005 | 23 | 99900% | 0.085527
CHILLERHEATERMODULE:Chiller Heater EIR Part Load Modifier Multiplier Unit 1 [](Hourly) | 0.001 | 0.005 | 33 | 99900% | 0.083185
CHILLERHEATERMODULE:Chiller Heater Condenser Inlet Temperature Unit 1 [C](Hourly) | 0.2 | -1 | 3281 | 168.4% | 15.0637
CHILLERHEATERMODULE:Chiller Heater Condenser Outlet Temperature Unit 1 [C](Hourly) | 0.2 | -1 | 3033 | 168.4% | 15.0637
CHILLERHEATERMODULE:Chiller Heater Condenser Mass Flow Rate Unit 1 [kg/s](Hourly) | 0.001 | 0.005 | 7 | 99900% | 0.044094
CHILLERHEATERMODULE:Chiller Heater Operation Mode Unit 2 [](Hourly) | 0.001 | 0.005 | 24 | 99900% | 0.16667
CHILLERHEATERMODULE:Chiller Heater Part Load Ratio Unit 2 [](Hourly) | 0.001 | 0.005 | 72 | 99900% | 0.083333
CHILLERHEATERMODULE:Chiller Heater Cycling Ratio Unit 2 [](Hourly) | 0.001 | 0.005 | 36 | 99900% | 0.083333
CHILLERHEATERMODULE:Chiller Heater Cooling Electric Power Unit 2 [W](Hourly) | 0.1 | 0.005 | 33 | 100% | 2499.5863
CHILLERHEATERMODULE:Chiller Heater Heating Electric Power Unit 2 [W](Hourly) | 0.1 | 0.005 | 70 | 99900% | 965.7772
CHILLERHEATERMODULE:Chiller Heater Cooling Rate Unit 2 [W](Hourly) | 0.1 | 0.005 | 72 | 99900% | 758.2444
CHILLERHEATERMODULE:Chiller Heater Evaporator Inlet Temperature Unit 2 [C](Hourly) | 0.2 | -1 | 41 | 37.51% | 4.3413
CHILLERHEATERMODULE:Chiller Heater Evaporator Outlet Temperature Unit 2 [C](Hourly) | 0.2 | -1 | 37 | 56.5% | 4.434
CHILLERHEATERMODULE:Chiller Heater Evaporator Mass Flow Rate Unit 2 [kg/s](Hourly) | 0.001 | 0.005 | 81 | 99900% | 0.17896
CHILLERHEATERMODULE:Chiller Heater Condenser Heat Transfer Rate Unit 2 [W](Hourly) | 0.1 | 0.005 | 446 | 99900% | 349.4486
CHILLERHEATERMODULE:Chiller Heater Capacity Temperature Modifier Multiplier Unit 2 [](Hourly) | 0.001 | 0.005 | 21 | 99900% | 0.081972
CHILLERHEATERMODULE:Chiller Heater EIR Temperature Modifier Multiplier Unit 2 [](Hourly) | 0.001 | 0.005 | 32 | 99900% | 0.085527
CHILLERHEATERMODULE:Chiller Heater EIR Part Load Modifier Multiplier Unit 2 [](Hourly) | 0.001 | 0.005 | 70 | 99900% | 0.083185
CHILLERHEATERMODULE:Chiller Heater Condenser Inlet Temperature Unit 2 [C](Hourly) | 0.2 | -1 | 3281 | 168.4% | 15.0637
CHILLERHEATERMODULE:Chiller Heater Condenser Outlet Temperature Unit 2 [C](Hourly) | 0.2 | -1 | 3044 | 168.4% | 15.0637
CHILLERHEATERMODULE:Chiller Heater Condenser Mass Flow Rate Unit 2 [kg/s](Hourly) | 0.001 | 0.005 | 57 | 99900% | 0.034023
CHILLERHEATERMODULE:Chiller Heater Operation Mode Unit 3 [](Hourly) | 0.001 | 0.005 | 70 | 99900% | 0.25
CHILLERHEATERMODULE:Chiller Heater Part Load Ratio Unit 3 [](Hourly) | 0.001 | 0.005 | 64 | 99900% | 0.0125
CHILLERHEATERMODULE:Chiller Heater Cycling Ratio Unit 3 [](Hourly) | 0.001 | 0.005 | 63 | 99900% | 0.00013392
CHILLERHEATERMODULE:Chiller Heater Cooling Electric Power Unit 3 [W](Hourly) | 0.1 | 0.005 | 90 | 99900% | 0.41606
CHILLERHEATERMODULE:Chiller Heater Heating Electric Power Unit 3 [W](Hourly) | 0.1 | 0.005 | 4 | 99900% | 3881.5471
CHILLERHEATERMODULE:Chiller Heater Cooling Rate Unit 3 [W](Hourly) | 0.1 | 0.005 | 81 | 99900% | 0.43353
CHILLERHEATERMODULE:Chiller Heater Evaporator Inlet Temperature Unit 3 [C](Hourly) | 0.2 | -1 | 1157 | 61.52% | 14.1669
CHILLERHEATERMODULE:Chiller Heater Evaporator Outlet Temperature Unit 3 [C](Hourly) | 0.2 | -1 | 1158 | 82.24% | 5.1183
CHILLERHEATERMODULE:Chiller Heater Evaporator Mass Flow Rate Unit 3 [kg/s](Hourly) | 0.001 | 0.005 | 1295 | 478394% | 0.2681
CHILLERHEATERMODULE:Chiller Heater Condenser Heat Transfer Rate Unit 3 [W](Hourly) | 0.1 | 0.005 | 92 | 99900% | 0.84959
CHILLERHEATERMODULE:Chiller Heater Capacity Temperature Modifier Multiplier Unit 3 [](Hourly) | 0.001 | 0.005 | 26 | 99900% | 0.081972
CHILLERHEATERMODULE:Chiller Heater EIR Temperature Modifier Multiplier Unit 3 [](Hourly) | 0.001 | 0.005 | 77 | 99900% | 0.085527
CHILLERHEATERMODULE:Chiller Heater EIR Part Load Modifier Multiplier Unit 3 [](Hourly) | 0.001 | 0.005 | 109 | 99900% | 0.083185
CHILLERHEATERMODULE:Chiller Heater Condenser Inlet Temperature Unit 3 [C](Hourly) | 0.2 | -1 | 3353 | 168.4% | 15.0637
CHILLERHEATERMODULE:Chiller Heater Condenser Outlet Temperature Unit 3 [C](Hourly) | 0.2 | -1 | 3585 | 168.4% | 15.0637
CHILLERHEATERMODULE:Chiller Heater Condenser Mass Flow Rate Unit 3 [kg/s](Hourly) | 0.001 | 0.005 | 89 | 99900% | 0.029478
5ZoneVAV-ChilledWaterStorage-Mixed_DCV_MaxZd | [5 empty] | Existing warnings
SimHVAC:HVAC System Solver Iteration Count [](Hourly) | 0.001 | 0.005 | 3 | 37.5% | 6 | ** Warning ** SimHVAC: Maximum iterations (25) exceeded for all HVAC loops, at RUN PERIOD 1, 01/03 08:00 - 08:15
HEATSYS1:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 2 | 5.924% | 1.38 | ** ~~~ ** The solution for one or more of the Air Loop HVAC systems did not appear to converge
COOLSYSSECONDARY:Plant Supply Side Unmet Demand Rate [W](Hourly) | 0.1 | 0.005 | 1 | 1.16% | 687.4443 | ** ~~~ ** ...use Output:Diagnostics,DisplayExtraWarnings; to show more details on each max iteration exceeded.
VAV WITH REHEAT_COOLC:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 3 | 0.6618% | 142.0276
VAV WITH REHEAT:Air System Outdoor Air Flow Fraction [](Hourly) | 0.001 | 0.005 | 2 | 1.413% | 0.0014736
5ZoneCoolingPanelBaseboardAuto | [5 empty] | Existing warnings
PLENUM-1:Zone Air System Sensible Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 625.9% | 1.2904 | Warning ** SimHVAC: Maximum iterations (20) exceeded for all HVAC loops, at RUN PERIOD 1, 01/01 08:15 - 08:20
PLENUM-1:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 5 | 11.57% | 4.1555 | ** ~~~ ** The solution for one or more of the Air Loop HVAC systems did not appear to converge
PLENUM-1:Zone Air Relative Humidity [%](Hourly) | 0.001 | 0.005 | 64 | 1.705% | 0.698 | ** ~~~ ** ...use Output:Diagnostics,DisplayExtraWarnings; to show more details on each max iteration exceeded.
MAIN HEATING COIL 1:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 31 | 100% | 147.7948
MAIN COOLING COIL 1:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 27 | 14.61% | 826.066
MAIN COOLING COIL 1:Cooling Coil Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 22 | 14.1% | 792.8698
SPACE2 COOLING PANEL:Cooling Panel Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 35 | 100% | 42.5877
SPACE2 COOLING PANEL:Cooling Panel Total System Cooling Rate [W](Hourly) | 0.1 | 0.005 | 36 | 100% | 20.4216
SPACE2 COOLING PANEL:Cooling Panel Convective Cooling Rate [W](Hourly) | 0.1 | 0.005 | 35 | 100% | 14.9057
SPACE2 COOLING PANEL:Cooling Panel Radiant Cooling Rate [W](Hourly) | 0.1 | 0.005 | 35 | 100% | 27.682
SPACE2 COOLING PANEL:Cooling Panel Total Cooling Energy [J](Hourly) | 0.001 | 0.005 | 35 | 100% | 153315.5798
SPACE2 COOLING PANEL:Cooling Panel Total System Cooling Energy [J](Hourly) | 0.001 | 0.005 | 36 | 100% | 73517.6964
SPACE2 COOLING PANEL:Cooling Panel Convective Cooling Energy [J](Hourly) | 0.001 | 0.005 | 35 | 100% | 53660.4529
SPACE2 COOLING PANEL:Cooling Panel Radiant Cooling Energy [J](Hourly) | 0.001 | 0.005 | 35 | 100% | 99655.1269
SPACE2 COOLING PANEL:Cooling Panel Water Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 3 | 100% | 0.00072537
SPACE2 COOLING PANEL:Cooling Panel Water Inlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 8.424% | 0.67832
SPACE2 COOLING PANEL:Cooling Panel Water Outlet Temperature [C](Hourly) | 0.2 | -1 | 21 | 57.2% | 5.3504
SPACE2-1 BASEBOARD:Baseboard Total Heating Rate [W](Hourly) | 0.1 | 0.005 | 4 | 364.6% | 0.60048
SPACE2-1 BASEBOARD:Baseboard Convective Heating Rate [W](Hourly) | 0.1 | 0.005 | 5 | 93.56% | 0.50484
SPACE2-1 BASEBOARD:Baseboard Radiant Heating Rate [W](Hourly) | 0.1 | 0.005 | 5 | 93.56% | 0.21636
SPACE2-1 BASEBOARD:Baseboard Total Heating Energy [J](Hourly) | 0.001 | 0.005 | 5 | 364.6% | 2161.7264
SPACE2-1 BASEBOARD:Baseboard Convective Heating Energy [J](Hourly) | 0.001 | 0.005 | 6 | 93.56% | 1817.415
SPACE2-1 BASEBOARD:Baseboard Radiant Heating Energy [J](Hourly) | 0.001 | 0.005 | 6 | 93.56% | 778.8921
CENTRAL CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 35 | 18.96% | 3347.6799
DualDuctVarVolDamper | [5 empty] | None
SimAir:Air System Simulation Maximum Iteration Count [](Hourly) | 0.001 | 0.005 | 1 | 0.813% | 1
ChangeoverBypassVAV_AirToAirHeatPump | [5 empty] | None
WEST ZONE:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 17 | 4.816% | 0.56572
WEST ZONE:Zone Predicted Sensible Load to Setpoint Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 16 | 34.82% | 0.081374
ZONE 1 VAV SYSTEM:Zone Air Terminal VAV Damper Position [](Hourly) | 0.001 | 0.005 | 45 | 3.64% | 0.0066518
MAIN DX HEATING COIL 1:Heating Coil Heating Energy [J](Hourly) | 0.001 | 0.005 | 11 | 24.92% | 0.095328
MAIN COOLING COIL 1:Cooling Coil Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 3 | 1.41% | 8.5554
MAIN COOLING COIL 1:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 3 | 1.41% | 8.5554
MAIN COOLING COIL 1:Cooling Coil Electric Power [W](Hourly) | 0.1 | 0.005 | 3 | 1.343% | 1.3949
MAIN COOLING COIL 1:Cooling Coil Runtime Fraction [](Hourly) | 0.001 | 0.005 | 1 | 1.448% | 0.0010506
CBVAV HEAT PUMP SYSTEM:Unitary System Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 65 | 13.34% | 5.3559
CBVAV HEAT PUMP SYSTEM:Unitary System Total Cooling Energy [J](Hourly) | 0.001 | 0.005 | 65 | 13.34% | 19281.3509
CBVAV HEAT PUMP SYSTEM:Unitary System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 65 | 13.34% | 5.3559
CBVAV HEAT PUMP SYSTEM:Unitary System Sensible Cooling Energy [J](Hourly) | 0.001 | 0.005 | 66 | 13.34% | 19281.3509
CBVAV HEAT PUMP SYSTEM:Unitary System Latent Cooling Energy [J](Hourly) | 0.001 | 0.005 | 1 | 99900% | 1.487e-08
CBVAV HEAT PUMP SYSTEM:Unitary System Bypass Air Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 107 | 59.51% | 0.11282
CBVAV HEAT PUMP SYSTEM:Unitary System Air Outlet Setpoint Temperature [C](Hourly) | 0.2 | -1 | 1 | 1.521% | 0.43052
ZONE 1 REHEAT AIR OUTLET NODE:System Node Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 42 | 3.64% | 0.0044681
ZONE 1 REHEAT AIR OUTLET NODE:System Node Standard Density Volume Flow Rate [m3/s](Hourly) | 0.001 | 0.005 | 40 | 3.64% | 0.0037149
5ZoneVAV-ChilledWaterStorage-Mixed_DCV_MultiPath | [5 empty] | Diffs in existing warning
CHILLED WATER STORAGE TANK 1:Chilled Water Thermal Storage Use Side Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 1 | 0.6094% | 0.0028512 | - ** Warning ** SimHVAC: Maximum iterations (25) exceeded for all HVAC loops, at RUN PERIOD 1, 06/20 10:00 - 10:15
CHILLED WATER STORAGE TANK 1:Chilled Water Thermal Storage Use Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.556% | 55.2317 | - ** ~~~ ** The solution for one or more of the Air Loop HVAC systems did not appear to converge
CHILLED WATER STORAGE TANK 1:Chilled Water Thermal Storage Use Side Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 1 | 0.556% | 198834.1347
SimHVAC:HVAC System Solver Iteration Count [](Hourly) | 0.001 | 0.005 | 3 | 61.29% | 19
HEATSYS1:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 2 | 2.09% | 1.2203
COOLSYSSECONDARY:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 3 | 1.966% | 3239.6072
VAV WITH REHEAT_COOLC:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 2 | 2.114% | 272.7063
VAV WITH REHEAT:Air System Outdoor Air Flow Fraction [](Hourly) | 0.001 | 0.005 | 2 | 1.673% | 0.0046757
HeatRecoveryPlantLoopAuto | [5 empty] | None
BIG WATER HEATER:Water Heater Use Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 4 | 100% | 22.0229
BIG WATER HEATER:Water Heater Use Side Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 4 | 100% | 79282.4734
BIG WATER HEATER:Water Heater Source Side Inlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 1.238% | 1.0987
BIG WATER HEATER:Water Heater Source Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 4 | 16.89% | 1956.478
BIG WATER HEATER:Water Heater Source Side Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 4 | 16.89% | 7043320.8186
BIG WATER HEATER:Water Heater Total Demand Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 20 | 132.5% | 1.9257
BIG WATER HEATER:Water Heater Total Demand Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 20 | 132.5% | 6932.5696
BIG WATER HEATER:Water Heater Heating Rate [W](Hourly) | 0.1 | 0.005 | 2 | 1.033% | 29.9804
BIG WATER HEATER:Water Heater Heating Energy [J](Hourly) | 0.001 | 0.005 | 2 | 1.033% | 107929.3873
BIG WATER HEATER:Water Heater Unmet Demand Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.8669% | 1.8195
BIG WATER HEATER:Water Heater Unmet Demand Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 1 | 0.8669% | 6550.2412
BIG WATER HEATER:Water Heater Venting Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 5 | 17.57% | 1978.5009
BIG WATER HEATER:Water Heater Venting Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 5 | 17.57% | 7122603.2921
BIG WATER HEATER:Water Heater Net Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 14 | 99900% | 3.0316e-13
BIG WATER HEATER:Water Heater Net Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 14 | 99900% | 1.0914e-09
BIG WATER HEATER:Water Heater Runtime Fraction [](Hourly) | 0.001 | 0.005 | 1 | 1.033% | 0.0024984
BIG WATER HEATER:Water Heater Part Load Ratio [](Hourly) | 0.001 | 0.005 | 1 | 1.033% | 0.0024984
BIG WATER HEATER:Water Heater Electric Power [W](Hourly) | 0.1 | 0.005 | 2 | 1.033% | 29.9804
BIG WATER HEATER:Water Heater Electric Energy [J](Hourly) | 0.001 | 0.005 | 2 | 1.033% | 107929.3873
WEST ZONE:Zone Air System Sensible Heating Rate [W](Hourly) | 0.1 | 0.005 | 18 | 12.01% | 0.55423
WEST ZONE:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 29 | 15.52% | 15.1538
CHILLED WATER LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 31 | 100% | 102.1475
CHILLED WATER LOOP:Plant Supply Side Inlet Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 11 | 100% | 0.002689
CHILLED WATER LOOP:Plant Supply Side Inlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 2.021% | 0.32714
CHILLED WATER LOOP:Plant Supply Side Outlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 23.93% | 3.0852
HOT WATER LOOP:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 4 | 100% | 14.074
Whole Building:Facility Total HVAC Electric Demand Power [W](Hourly) | 0.1 | 0.005 | 4 | 10.43% | 299.5242
Whole Building:Facility Total Electric Demand Power [W](Hourly) | 0.1 | 0.005 | 4 | 10.02% | 299.5242
SOLAR TURBINE:Generator Produced Thermal Rate [W](Hourly) | 0.1 | 0.005 | 4 | 20% | 2564.8931
SOLAR TURBINE:Generator Heat Recovery Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 4 | 20% | 0.078492
REHEAT COIL ZONE 1:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 8 | 5.357% | 19.1448
DETAILED COOLING COIL:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 35 | 100% | 105.9787
SimAir:Air System Simulation Maximum Iteration Count [](Hourly) | 0.001 | 0.005 | 13 | 99900% | 3
BIG CHILLER:Chiller Drive Shaft Power [W](Hourly) | 0.1 | 0.005 | 31 | 100% | 28.1522
BIG CHILLER:Chiller Drive Shaft Energy [J](Hourly) | 0.001 | 0.005 | 31 | 100% | 101347.9038
BIG CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 31 | 100% | 102.1475
BIG CHILLER:Chiller Evaporator Inlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 2.021% | 0.32714
BIG CHILLER:Chiller Evaporator Outlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 23.93% | 3.0852
BIG CHILLER:Chiller Evaporator Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 11 | 100% | 0.002689
BIG CHILLER:Chiller Condenser Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 31 | 100% | 130.2997
BIG CHILLER:Chiller Condenser Inlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 2.407% | 0.24074
BIG CHILLER:Chiller Condenser Outlet Temperature [C](Hourly) | 0.2 | -1 | 4 | 2.407% | 0.24074
BIG CHILLER:Chiller Condenser Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 4 | 100% | 0.67504
BIG CHILLER:Chiller Diesel Rate [W](Hourly) | 0.1 | 0.005 | 31 | 100% | 73.7314
BIG CHILLER:Chiller Diesel Energy [J](Hourly) | 0.001 | 0.005 | 31 | 100% | 265433.2107
BIG CHILLER:Chiller Exhaust Temperature [C](Hourly) | 0.2 | -1 | 4 | 100% | 50.0255
BIG CHILLER:Chiller Heat Recovery Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 4 | 100% | 0.078492
BIG CHILLER:Chiller Jacket Recovered Heat Rate [W](Hourly) | 0.1 | 0.005 | 9 | 8.845% | 19.1333
BIG CHILLER:Chiller Jacket Recovered Heat Energy [J](Hourly) | 0.001 | 0.005 | 9 | 8.845% | 68879.862
BIG CHILLER:Chiller Lube Recovered Heat Rate [W](Hourly) | 0.1 | 0.005 | 9 | 8.845% | 46.7913
BIG CHILLER:Chiller Lube Recovered Heat Energy [J](Hourly) | 0.001 | 0.005 | 9 | 8.845% | 168448.749
BIG CHILLER:Chiller Exhaust Recovered Heat Rate [W](Hourly) | 0.1 | 0.005 | 9 | 8.845% | 11.3081
BIG CHILLER:Chiller Exhaust Recovered Heat Energy [J](Hourly) | 0.001 | 0.005 | 9 | 8.845% | 40709.1384
BIG CHILLER:Chiller Total Recovered Heat Rate [W](Hourly) | 0.1 | 0.005 | 9 | 8.845% | 77.2327
BIG CHILLER:Chiller Total Recovered Heat Energy [J](Hourly) | 0.001 | 0.005 | 9 | 8.845% | 278037.7495
CIRC PUMP:Pump Fluid Heat Gain Rate [W](Hourly) | 0.1 | 0.005 | 20 | 100% | 1.0353
5ZoneIceStorage | [5 empty] | Existing warnings
ICE TANK:Ice Thermal Storage Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 1 | 6.667% | 0.15609 | ** Warning ** SimHVAC: Maximum iterations (30) exceeded for all HVAC loops, at RUN PERIOD 1, 02/05 09:38 - 09:41
Electricity:Facility [J](Hourly) | 0.001 | 0.005 | 1 | 2.069% | 808667.3399
Electricity:Plant [J](Hourly) | 0.001 | 0.005 | 3 | 61.43% | 808667.3399
ICE TANK:Ice Thermal Storage Requested Load [W](Hourly) | 0.1 | 0.005 | 8 | 74.93% | 201.942
TermRhSingleHeatCoolNoDB | [5 empty] | None
EAST ZONE:Zone Air System Sensible Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.8781% | 0.00080588
5ZoneVAV-ChilledWaterStorage-Stratified | [5 empty] | Existing warnings
SimAir:Air System Simulation Iteration Count [](Hourly) | 0.001 | 0.005 | 2 | 1.562% | 1 | ** Warning ** The design coil load is zero for Coil:Heating:Water VAV WITH REHEAT_HEATC
RefBldgSuperMarketNew2004_Chicago | [5 empty] | None
Heating:Gas [J](Hourly) | 0.001 | 0.005 | 1 | 1.821% | 444666.3396
PSZ-AC:5:Air System Total Heating Energy [J](Hourly) | 0.001 | 0.005 | 1 | 2.73% | 349490.2144
ChangeoverBypassVAV_AirToAir | [5 empty] | None
MAIN COOLING COIL 1:Cooling Coil Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 1.328% | 8.0771
MAIN COOLING COIL 1:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 1.328% | 8.0771
MAIN COOLING COIL 1:Cooling Coil Electric Power [W](Hourly) | 0.1 | 0.005 | 1 | 1.256% | 1.307
GASHEAT CBVAV SYSTEM:Unitary System Air Outlet Setpoint Temperature [C](Hourly) | 0.2 | -1 | 1 | 1.552% | 0.43906
WEST ZONE:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 12 | 3.825% | 1.1341
WEST ZONE:Zone Predicted Sensible Load to Setpoint Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 16 | 39.46% | 0.077968
ZONE 1 REHEAT AIR OUTLET NODE:System Node Standard Density Volume Flow Rate [m3/s](Hourly) | 0.001 | 0.005 | 30 | 8.735% | 0.0079021
ZONE 1 REHEAT AIR OUTLET NODE:System Node Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 32 | 8.735% | 0.0095042
ZONE 1 VAV SYSTEM:Zone Air Terminal VAV Damper Position [](Hourly) | 0.001 | 0.005 | 40 | 8.735% | 0.014149
GASHEAT CBVAV SYSTEM:Unitary System Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 68 | 10.64% | 8.0771
GASHEAT CBVAV SYSTEM:Unitary System Total Cooling Energy [J](Hourly) | 0.001 | 0.005 | 68 | 10.64% | 29077.5039
GASHEAT CBVAV SYSTEM:Unitary System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 68 | 10.64% | 8.0771
GASHEAT CBVAV SYSTEM:Unitary System Sensible Cooling Energy [J](Hourly) | 0.001 | 0.005 | 68 | 10.64% | 29077.5039
GASHEAT CBVAV SYSTEM:Unitary System Bypass Air Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 98 | 59.51% | 0.11282
_DualDuctConstVolDamperMultizoneAverageSetPointManager | [5 empty] | Diffs in existing warnings
SimAir:Air System Simulation Maximum Iteration Count [](Hourly) | 0.001 | 0.005 | 1 | 4.762% | 1
ChangeoverBypassVAV | [5 empty] | None
GASHEAT CBVAV SYSTEM:Unitary System Total Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 1.685% | 0.0072553
GASHEAT CBVAV SYSTEM:Unitary System Latent Cooling Energy [J](Hourly) | 0.001 | 0.005 | 1 | 99900% | 2.4556e-09
AIR LOOP INLET NODE:System Node Temperature [C](Hourly) | 0.2 | -1 | 1 | 0.7829% | 0.22997
GASHEAT CBVAV SYSTEM:Unitary System Air Outlet Setpoint Temperature [C](Hourly) | 0.2 | -1 | 2 | 1.21% | 0.34821
GASHEAT CBVAV SYSTEM:Unitary System Total Heating Energy [J](Hourly) | 0.001 | 0.005 | 3 | 1.685% | 26.119
ACDXCOIL 2:Cooling Coil Runtime Fraction [](Hourly) | 0.001 | 0.005 | 9 | 99900% | 0.015406
GASHEAT CBVAV SYSTEM:Unitary System Electric Power [W](Hourly) | 0.1 | 0.005 | 9 | 99900% | 344.0273
GASHEAT CBVAV SYSTEM:Unitary System Electric Energy [J](Hourly) | 0.001 | 0.005 | 9 | 99900% | 1238498.2986
GASHEAT CBVAV SYSTEM:Unitary System Fan Part Load Ratio [](Hourly) | 0.001 | 0.005 | 9 | 99900% | 0.16667
GASHEAT CBVAV SYSTEM:Unitary System Compressor Part Load Ratio [](Hourly) | 0.001 | 0.005 | 9 | 99900% | 0.01328
ACDXCOIL 2:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 12 | 99900% | 307.0192
ACDXCOIL 2:Cooling Coil Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 12 | 99900% | 307.0192
ACDXCOIL 2:Cooling Coil Electric Power [W](Hourly) | 0.1 | 0.005 | 14 | 99900% | 77.9746
ZONE 1 VAV SYSTEM:Zone Air Terminal VAV Damper Position [](Hourly) | 0.001 | 0.005 | 35 | 99900% | 0.041667
ZONE 1 REHEAT AIR OUTLET NODE:System Node Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 35 | 99900% | 0.027988
WEST ZONE:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 49 | 99900% | 22.7087
WEST ZONE:Zone Predicted Sensible Load to Setpoint Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 55 | 99900% | 0.64637
GASHEAT CBVAV SYSTEM:Unitary System Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 66 | 99900% | 40.9665
GASHEAT CBVAV SYSTEM:Unitary System Total Cooling Energy [J](Hourly) | 0.001 | 0.005 | 66 | 99900% | 147479.3696
GASHEAT CBVAV SYSTEM:Unitary System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 66 | 99900% | 40.9665
GASHEAT CBVAV SYSTEM:Unitary System Sensible Cooling Energy [J](Hourly) | 0.001 | 0.005 | 66 | 99900% | 147479.3696
GASHEAT CBVAV SYSTEM:Unitary System Bypass Air Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 100 | 99900% | 0.16717
ChangeoverBypassVAV_MaxTemp | [5 empty] | None
ACDXCOIL 2:Cooling Coil Runtime Fraction [](Hourly) | 0.001 | 0.005 | 1 | 16.41% | 0.014941
GASHEAT CBVAV SYSTEM:Unitary System Total Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 2.804% | 0.97761
GASHEAT CBVAV SYSTEM:Unitary System Latent Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 99900% | 5.2106e-13
GASHEAT CBVAV SYSTEM:Unitary System Electric Power [W](Hourly) | 0.1 | 0.005 | 1 | 16.59% | 338.0988
GASHEAT CBVAV SYSTEM:Unitary System Electric Energy [J](Hourly) | 0.001 | 0.005 | 1 | 16.59% | 1217155.7069
GASHEAT CBVAV SYSTEM:Unitary System Fan Part Load Ratio [](Hourly) | 0.001 | 0.005 | 1 | 16.67% | 0.16667
GASHEAT CBVAV SYSTEM:Unitary System Compressor Part Load Ratio [](Hourly) | 0.001 | 0.005 | 1 | 16.4% | 0.012873
ZONE 1 REHEAT AIR OUTLET NODE:System Node Temperature [C](Hourly) | 0.2 | -1 | 1 | 1.113% | 0.31199
GASHEAT CBVAV SYSTEM:Unitary System Total Heating Energy [J](Hourly) | 0.001 | 0.005 | 2 | 2.804% | 3519.3818
GASHEAT CBVAV SYSTEM:Unitary System Sensible Heating Rate [W](Hourly) | 0.1 | 0.005 | 2 | 0.6181% | 0.17941
GASHEAT CBVAV SYSTEM:Unitary System Sensible Heating Energy [J](Hourly) | 0.001 | 0.005 | 2 | 0.6181% | 645.8919
GASHEAT CBVAV SYSTEM:Unitary System Air Outlet Setpoint Temperature [C](Hourly) | 0.2 | -1 | 2 | 1.36% | 0.39074
ACDXCOIL 2:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 3 | 16.43% | 291.1917
ACDXCOIL 2:Cooling Coil Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 3 | 16.43% | 291.1917
GASHEAT CBVAV SYSTEM:Unitary System Latent Cooling Energy [J](Hourly) | 0.001 | 0.005 | 3 | 99900% | 1.8758e-09
ACDXCOIL 2:Cooling Coil Electric Power [W](Hourly) | 0.1 | 0.005 | 4 | 16.31% | 72.0461
WEST ZONE:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 18 | 14.75% | 10.5588
WEST ZONE:Zone Predicted Sensible Load to Setpoint Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 19 | 99900% | 0.042209
ZONE 1 REHEAT AIR OUTLET NODE:System Node Standard Density Volume Flow Rate [m3/s](Hourly) | 0.001 | 0.005 | 52 | 15.48% | 0.0047059
ZONE 1 REHEAT AIR OUTLET NODE:System Node Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 54 | 15.48% | 0.0056599
ZONE 1 VAV SYSTEM:Zone Air Terminal VAV Damper Position [](Hourly) | 0.001 | 0.005 | 57 | 15.48% | 0.0084262
GASHEAT CBVAV SYSTEM:Unitary System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 70 | 14.71% | 9.7494
GASHEAT CBVAV SYSTEM:Unitary System Sensible Cooling Energy [J](Hourly) | 0.001 | 0.005 | 70 | 14.71% | 35097.6865
GASHEAT CBVAV SYSTEM:Unitary System Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 71 | 14.71% | 9.7494
GASHEAT CBVAV SYSTEM:Unitary System Total Cooling Energy [J](Hourly) | 0.001 | 0.005 | 71 | 14.71% | 35097.6865
GASHEAT CBVAV SYSTEM:Unitary System Bypass Air Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 117 | 59.51% | 0.11282
HeatRecoveryElectricChiller | [5 empty] | None
WEST ZONE:Zone Mean Air Temperature [C](Hourly) | 0.2 | -1 | 2 | 2.734% | 0.51799
WEST ZONE:Zone Air System Sensible Heating Rate [W](Hourly) | 0.1 | 0.005 | 11 | 146.2% | 5.0719
WEST ZONE:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 10 | 11.14% | 174.7752
WEST ZONE:Zone Air Temperature [C](Hourly) | 0.2 | -1 | 2 | 2.734% | 0.51799
SimHVAC:HVAC System Solver Iteration Count [](Hourly) | 0.001 | 0.005 | 10 | 25% | 2
CHILLED WATER LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 29 | 6.492% | 693.5793
CHILLED WATER LOOP:Plant Supply Side Inlet Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 40 | 5.659% | 0.016151
CHILLED WATER LOOP:Plant Supply Side Inlet Temperature [C](Hourly) | 0.2 | -1 | 14 | 1.35% | 0.20995
CHILLED WATER LOOP:Plant Supply Side Outlet Temperature [C](Hourly) | 0.2 | -1 | 14 | 1.35% | 0.20995
HOT WATER LOOP:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 124 | 54.33% | 26271.5674
REHEAT COIL ZONE 1:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 72 | 99900% | 2.3405
DETAILED COOLING COIL:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 26 | 6.444% | 688.6471
SUPPLY FAN 1:Fan Electric Power [W](Hourly) | 0.1 | 0.005 | 0 | 4.081e-14% | 4.5475e-13
SimAir:Air System Simulation Maximum Iteration Count [](Hourly) | 0.001 | 0.005 | 26 | 99900% | 3
BIG WATER HEATER:Water Heater Tank Temperature [C](Hourly) | 0.2 | -1 | 256 | 19.16% | 4.7793
BIG WATER HEATER:Water Heater Heat Loss Rate [W](Hourly) | 0.1 | 0.005 | 319 | 1771% | 3.4609
BIG WATER HEATER:Water Heater Heat Loss Energy [J](Hourly) | 0.001 | 0.005 | 450 | 1771% | 12459.0702
BIG WATER HEATER:Water Heater Use Side Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 112 | 38.89% | 0.00042313
BIG WATER HEATER:Water Heater Use Side Inlet Temperature [C](Hourly) | 0.2 | -1 | 197 | 8.682% | 1.7566
BIG WATER HEATER:Water Heater Use Side Outlet Temperature [C](Hourly) | 0.2 | -1 | 256 | 19.16% | 4.7793
BIG WATER HEATER:Water Heater Use Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 124 | 939.9% | 4797.0479
BIG WATER HEATER:Water Heater Use Side Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 125 | 939.9% | 17269372.3901
BIG WATER HEATER:Water Heater Source Side Inlet Temperature [C](Hourly) | 0.2 | -1 | 235 | 9.204% | 2.2055
BIG WATER HEATER:Water Heater Source Side Outlet Temperature [C](Hourly) | 0.2 | -1 | 256 | 19.16% | 4.7793
BIG WATER HEATER:Water Heater Source Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 137 | 4004% | 1396.4625
BIG WATER HEATER:Water Heater Source Side Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 137 | 4004% | 5027264.8398
BIG WATER HEATER:Water Heater Total Demand Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 343 | 62617% | 6837.5404
BIG WATER HEATER:Water Heater Total Demand Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 438 | 62617% | 24615145.4417
BIG WATER HEATER:Water Heater Heating Rate [W](Hourly) | 0.1 | 0.005 | 84 | 99900% | 2368.2878
BIG WATER HEATER:Water Heater Heating Energy [J](Hourly) | 0.001 | 0.005 | 84 | 99900% | 8525835.9655
BIG WATER HEATER:Water Heater Unmet Demand Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 49 | 99900% | 6546.3083
BIG WATER HEATER:Water Heater Unmet Demand Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 49 | 99900% | 23566709.7986
BIG WATER HEATER:Water Heater Net Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 356 | 9336% | 1061.2872
BIG WATER HEATER:Water Heater Net Heat Transfer Energy [J](Hourly) | 0.001 | 0.005 | 453 | 9336% | 3820633.8463
BIG WATER HEATER:Water Heater Cycle On Count [](Hourly) | 0.001 | 0.005 | 50 | 99900% | 1
BIG WATER HEATER:Water Heater Runtime Fraction [](Hourly) | 0.001 | 0.005 | 82 | 99900% | 0.067665
BIG WATER HEATER:Water Heater Part Load Ratio [](Hourly) | 0.001 | 0.005 | 82 | 99900% | 0.067665
BIG WATER HEATER:Water Heater Electric Power [W](Hourly) | 0.1 | 0.005 | 84 | 99900% | 2631.4309
BIG WATER HEATER:Water Heater Electric Energy [J](Hourly) | 0.001 | 0.005 | 84 | 99900% | 9473151.0728
BIG CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 29 | 6.492% | 693.5793
BIG CHILLER:Chiller Evaporator Inlet Temperature [C](Hourly) | 0.2 | -1 | 14 | 1.35% | 0.20995
BIG CHILLER:Chiller Evaporator Outlet Temperature [C](Hourly) | 0.2 | -1 | 14 | 1.35% | 0.20995
BIG CHILLER:Chiller Evaporator Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 40 | 5.659% | 0.016151
BIG CHILLER:Chiller Condenser Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 46 | 11.42% | 1513.2129
BIG CHILLER:Chiller Condenser Inlet Temperature [C](Hourly) | 0.2 | -1 | 0 | 0.6058% | 0.090287
BIG CHILLER:Chiller Condenser Outlet Temperature [C](Hourly) | 0.2 | -1 | 12 | 3.831% | 0.81367
BIG CHILLER:Chiller Condenser Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 0 | 2.221e-14% | 1.1102e-16
BIG CHILLER:Chiller Total Recovered Heat Rate [W](Hourly) | 0.1 | 0.005 | 50 | 820.4% | 130.8599
BIG CHILLER:Chiller Total Recovered Heat Energy [J](Hourly) | 0.001 | 0.005 | 51 | 820.4% | 471095.6928
BIG CHILLER:Chiller Heat Recovery Inlet Temperature [C](Hourly) | 0.2 | -1 | 263 | 10.48% | 2.1189
BIG CHILLER:Chiller Heat Recovery Outlet Temperature [C](Hourly) | 0.2 | -1 | 259 | 10.48% | 2.1189
BIG CHILLER:Chiller Heat Recovery Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 0 | 2.053e-14% | 1.1102e-16
CIRC PUMP:Pump Fluid Heat Gain Rate [W](Hourly) | 0.1 | 0.005 | 40 | 5.66% | 6.395
5ZoneWaterLoopHeatPump | [5 empty] | Diffs in details of existing warnings
SPACE1-1:Zone Air System Sensible Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 100% | 25.0184 | ************* ** Warning ** WaterToAir Heat pump:cooling [HEAT PUMP COOLING MODE AHU3] shut off on high pressure > 4000000
SPACE1-1:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 2.32% | 27.902 | - ************* ** ~~~ ** This error occurred 163 total times;
AHU 1 SUPPLY FAN:Fan Electric Power [W](Hourly) | 0.1 | 0.005 | 1 | 43.7% | 146.4177 | + ************* ** ~~~ ** This error occurred 160 total times;
HEAT PUMP COOLING MODE AHU1:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 2.712% | 54.1851
HEAT PUMP COOLING MODE AHU1:Cooling Coil Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 3.528% | 49.8625
HEAT PUMP COOLING MODE AHU1:Cooling Coil Source Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 1 | 3.092% | 99.2969
HEAT PUMP COOLING MODE AHU1:Cooling Coil Part Load Ratio [](Hourly) | 0.001 | 0.005 | 1 | 3.22% | 0.002859
HEAT PUMP COOLING MODE AHU1:Cooling Coil Runtime Fraction [](Hourly) | 0.001 | 0.005 | 1 | 1.853% | 0.002077
HEAT PUMP COOLING MODE AHU1:Cooling Coil Air Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 1 | 50.08% | 0.2027
HEAT PUMP COOLING MODE AHU1:Cooling Coil Air Outlet Temperature [C](Hourly) | 0.2 | -1 | 1 | 3.18% | 0.59899
HEAT PUMP COOLING MODE AHU1:Cooling Coil Source Side Inlet Temperature [C](Hourly) | 0.2 | -1 | 1 | 1.327% | 0.81252
HEAT PUMP COOLING MODE AHU1:Cooling Coil Source Side Outlet Temperature [C](Hourly) | 0.2 | -1 | 1 | 0.4135% | 0.27635
AHU 1 DXAC HEAT PUMP:Unitary System Fan Part Load Ratio [](Hourly) | 0.001 | 0.005 | 1 | 50.08% | 0.086192
AHU 1 DXAC HEAT PUMP:Unitary System Compressor Part Load Ratio [](Hourly) | 0.001 | 0.005 | 1 | 50.08% | 0.086192
AHU 1 DXAC HEAT PUMP:Unitary System Requested Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 13.89% | 189.1196
CENTRAL CHILLER:Chiller Evaporator Inlet Temperature [C](Hourly) | 0.2 | -1 | 1 | 0.387% | 0.25885
CENTRAL BOILER:Boiler Inlet Temperature [C](Hourly) | 0.2 | -1 | 1 | 0.387% | 0.25885
CENTRAL BOILER:Boiler Outlet Temperature [C](Hourly) | 0.2 | -1 | 1 | 0.387% | 0.25885
PLANT CIRC PUMP:Pump Outlet Temperature [C](Hourly) | 0.2 | -1 | 1 | 0.387% | 0.25885
CENTRAL CHILLER:Chiller Electric Power [W](Hourly) | 0.1 | 0.005 | 2 | 1.406% | 169.6301
CENTRAL CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 3 | 2.11% | 20.6228
CENTRAL CHILLER:Chiller Condenser Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 3 | 1.566% | 670.84
SINGLE WATER PLANT LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 4 | 3.388% | 2838.0991
CENTRAL CHILLER:Chiller Evaporator Outlet Temperature [C](Hourly) | 0.2 | -1 | 6 | 42.02% | 14.0817
CENTRAL CHILLER:Chiller Evaporator Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 6 | 26.05% | 0.31346
TermRhDualSetpointWithDB | [5 empty] | None
EAST ZONE:Zone Air System Sensible Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 1.63% | 0.0015434
HeatPumpWaterHeater | [5 empty] | Existing warnings
SPACE1-1 ZONE COIL:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 2 | 1.878% | 0.34904 | ** Warning ** Plant Loop: CONDENSER WATER LOOP Demand Side is storing excess heat the majority of the time.
ZONE4BHPWHDXCOIL:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 2 | 2.19% | 0.19822
ZONE4BHPWHTANK:Water Heater Source Side Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 2 | 2.174% | 0.3349
ZONE4BHPWHDXCOIL:Cooling Coil Total Water Heating Rate [W](Hourly) | 0.1 | 0.005 | 2 | 2.174% | 0.3345
ZONE4BHPWHDXCOIL:Cooling Coil Water Heating Electric Power [W](Hourly) | 0.1 | 0.005 | 2 | 1.964% | 0.17112
HPWHPLANTTANK:Water Heater Use Side Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 82 | 99900% | 0.0020378
RefrigeratedWarehouse | [5 empty] | Diffs in details of existing warnings
FREEZER_1:Refrigeration Zone Air Chiller Sensible Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.7156% | 584.4699 | ** Warning ** Zone Air Heat Balance is out of balance for zone named SUBFREEZER
FREEZER_1AIRCHILLER_1:Refrigeration Zone Air Chiller Frost Accumulation Mass [kg](Hourly) | 0.001 | 0.005 | 1 | 0.8157% | 0.12827 | - ** ~~~ ** Zone Air Heat Balance Deviation Rate is more than 8255.9 {W}
FREEZER_1AIRCHILLER_2:Refrigeration Zone Air Chiller Zone Heating Rate [W](Hourly) | 0.1 | 0.005 | 1 | 0.5715% | 54.0996 | + ** ~~~ ** Zone Air Heat Balance Deviation Rate is more than 8256.0 {W}
LOWTEMP001BITZER_OSNA8591_K:Refrigeration Air Chiller System Compressor Electric Power [W](Hourly) | 0.1 | 0.005 | 2 | 0.952% | 370.9803
FREEZER_1LOWTEMPSYSTEM:Refrigeration Air Chiller System Total Compressor Electric Power [W](Hourly) | 0.1 | 0.005 | 2 | 0.952% | 370.9803
FREEZER_1AIRCHILLER_2:Refrigeration Zone Air Chiller Total Electric Power [W](Hourly) | 0.1 | 0.005 | 3 | 20% | 370.9235
COOLER_2:Zone Mixing Latent Heat Gain Energy [J](Hourly) | 0.001 | 0.005 | 5 | 105% | 53.3247
FREEZER_1AIRCHILLER_2:Refrigeration Zone Air Chiller Sensible Heat Ratio [](Hourly) | 0.001 | 0.005 | 5 | 17.72% | 0.10171
FREEZER_1AIRCHILLER_2:Refrigeration Zone Air Chiller Zone Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 6 | 7.979% | 223.7663
COOLER_1UNITHEAT:Zone Unit Heater Heating Rate [W](Hourly) | 0.1 | 0.005 | 12 | 11.03% | 39.6984
COOLER_2:Zone Mixing Latent Heat Loss Energy [J](Hourly) | 0.001 | 0.005 | 32 | 28.95% | 158.8278
5ZoneVAV-ChilledWaterStorage-Mixed | [5 empty] | Diffs in details of existing warnings
SimHVAC:HVAC System Solver Iteration Count [](Hourly) | 0.001 | 0.005 | 7 | 77.14% | 27 | - ** Warning ** SimHVAC: Maximum iterations (25) exceeded for all HVAC loops, at ANNUAL, 07/11 16:00 - 16:15
HEATSYS1:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 1 | 3.706% | 0.82198 | - ** ~~~ ** The solution for one or more of the Air Loop HVAC systems did not appear to converge
VAV WITH REHEAT_COOLC:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 2 | 0.6993% | 148.5157 | - ** Warning ** SimHVAC: Maximum iterations (25) exceeded for all HVAC loops, at ANNUAL, 07/21 12:00 - 12:15
- ** ~~~ ** The solution for one or more of the Air Loop HVAC systems did not appear to converge
CompSetPtControl | [5 empty] | None
CHILLED WATER LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 87 | 185.1% | 5094.1442
CHILLED WATER LOOP:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 3 | 100% | 29.3695
LITTLE CHILLER:Chiller Electric Power [W](Hourly) | 0.1 | 0.005 | 61 | 99900% | 1119.463
LITTLE CHILLER:Chiller Evaporator Cooling Rate [W](Hourly) | 0.1 | 0.005 | 57 | 99900% | 3750
LITTLE CHILLER:Chiller Evaporator Inlet Temperature [C](Hourly) | 0.2 | -1 | 2360 | 12.37% | 0.91013
LITTLE CHILLER:Chiller Evaporator Outlet Temperature [C](Hourly) | 0.2 | -1 | 2370 | 81.4% | 3.1023
LITTLE CHILLER:Chiller Evaporator Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 57 | 99900% | 0.27497
LITTLE CHILLER:Chiller Condenser Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 57 | 99900% | 4869.463
LITTLE CHILLER:Chiller Condenser Inlet Temperature [C](Hourly) | 0.2 | -1 | 74 | 78.24% | 8.3999
LITTLE CHILLER:Chiller Condenser Outlet Temperature [C](Hourly) | 0.2 | -1 | 95 | 78.24% | 8.3999
LITTLE CHILLER:Chiller Condenser Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 78 | 99900% | 1.0999
HVACTemplate-5ZoneFanCoil-DOAS | [5 empty] | Diffs in details of existing warnings
SPACE3-1:Zone Air System Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 1.055% | 22.7578
SPACE4-1:Zone Air Relative Humidity [%](Hourly) | 0.001 | 0.005 | 3 | 3.299% | 1.8565
HOT WATER LOOP HOT WATER LOOP:Plant Supply Side Outlet Temperature [C](Hourly) | 0.2 | -1 | 11 | 0.601% | 0.38989
SPACE4-1 HEATING COIL:Heating Coil Heating Rate [W](Hourly) | 0.1 | 0.005 | 2 | 25.44% | 25.2158
SPACE1-1 COOLING COIL:Cooling Coil Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 5.355% | 2.3085
SPACE1-1 COOLING COIL:Cooling Coil Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 2 | 2.024% | 9.7387
DOAS HEAT RECOVERY:Heat Exchanger Sensible Cooling Rate [W](Hourly) | 0.1 | 0.005 | 1 | 9.604% | 2.7166
DOAS HEAT RECOVERY:Heat Exchanger Latent Cooling Rate [W](Hourly) | 0.1 | 0.005 | 2 | 1.362% | 6.9651
DOAS HEAT RECOVERY:Heat Exchanger Total Cooling Rate [W](Hourly) | 0.1 | 0.005 | 2 | 0.787% | 4.2485
MAIN BOILER:Boiler Heating Rate [W](Hourly) | 0.1 | 0.005 | 4 | 8.051% | 8.4703
MAIN BOILER:Boiler Gas Rate [W](Hourly) | 0.1 | 0.005 | 4 | 7.889% | 10.6458
HP_wICSSolarCollector | [5 empty] | None
COLLECTOR 1:Solar Collector Overall Top Heat Loss Coefficient [W/m2-C](Hourly) | 0.001 | 0.005 | 1 | 0.8325% | 0.018175
CentralChillerHeaterSystem_Cooling_Heating | [5 empty] | Existing warnings
VERTICAL GROUND HEAT EXCHANGER:Ground Heat Exchanger Heat Transfer Rate [W](Hourly) | 0.1 | 0.005 | 1027 | 99900% | 310.0938 | ** Warning ** Missing temperature setpoint on cooling side for CentralHeatPumpSystem named CHILLERBANK
VERTICAL GROUND HEAT EXCHANGER:Ground Heat Exchanger Inlet Temperature [C](Hourly) | 0.2 | -1 | 3512 | 79.33% | 13.2549 | ** ~~~ ** A temperature setpoint is needed at the outlet node of a CentralHeatPumpSystem, use a SetpointManager
VERTICAL GROUND HEAT EXCHANGER:Ground Heat Exchanger Outlet Temperature [C](Hourly) | 0.2 | -1 | 3512 | 79.33% | 13.2549 | ** ~~~ ** The overall loop setpoint will be assumed for CentralHeatPumpSystem. The simulation continues ...
VERTICAL GROUND HEAT EXCHANGER:Ground Heat Exchanger Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 693 | 99900% | 0.67243 | ** Warning ** Missing temperature setpoint on heating side for CentralHeatPumpSystem named CHILLERBANK
CHILLED WATER LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly) | 0.1 | 0.005 | 919 | 30.89% | 4966.2741 | ** ~~~ ** A temperature setpoint is needed at the outlet node of a CentralHeatPumpSystem, use a SetpointManager
CHILLED WATER LOOP:Plant Supply Side Unmet Demand Rate [W](Hourly) | 0.1 | 0.005 | 908 | 99900% | 713.7319 | ** ~~~ ** The overall loop setpoint will be assumed for CentralHeatPumpSystem. The simulation continues ...
HOT WATER LOOP:Plant Supply Side Heating Demand Rate [W](Hourly) | 0.1 | 0.005 | 209 | 75.85% | 152.1504
CHILLERBANK:Chiller Heater System Cooling Electric Energy [J](Hourly) | 0.001 | 0.005 | 947 | 86.53% | 17643616.8197
CHILLERBANK:Chiller Heater System Heating Electric Energy [J](Hourly) | 0.001 | 0.005 | 19 | 99900% | 5550940.7524
CHILLERBANK:Chiller Heater System Cooling Electric Power [W](Hourly) | 0.1 | 0.005 | 947 | 86.53% | 4901.0047
CHILLERBANK:Chiller Heater System Heating Electric Power [W](Hourly) | 0.1 | 0.005 | 19 | 99900% | 1541.928
CHILLERBANK:Chiller Heater System Cooling Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 179 | 28.48% | 0.20849
CHILLERBANK:Chiller Heater System Source Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 172 | 99900% | 0.22414
CHILLERBANK:Chiller Heater System Cooling Inlet Temperature [C](Hourly) | 0.2 | -1 | 1078 | 14.55% | 1.8015
CHILLERBANK:Chiller Heater System Heating Inlet Temperature [C](Hourly) | 0.2 | -1 | 3720 | 1.178% | 0.67875
CHILLERBANK:Chiller Heater System Source Inlet Temperature [C](Hourly) | 0.2 | -1 | 2860 | 121.1% | 12.8727
CHILLERBANK:Chiller Heater System Cooling Outlet Temperature [C](Hourly) | 0.2 | -1 | 1073 | 9.977% | 0.70672
CHILLERBANK:Chiller Heater System Heating Outlet Temperature [C](Hourly) | 0.2 | -1 | 3728 | 1.178% | 0.67875
CHILLERBANK:Chiller Heater System Source Outlet Temperature [C](Hourly) | 0.2 | -1 | 2885 | 121.1% | 12.8727
CHILLERHEATERMODULE 1:Chiller Heater Part Load Ratio Unit 1 [](Hourly) | 0.001 | 0.005 | 774 | 8.203% | 0.039971
CHILLERHEATERMODULE 1:Chiller Heater Cooling Electric Power Unit 1 [W](Hourly) | 0.1 | 0.005 | 730 | 6.619% | 249.78
CHILLERHEATERMODULE 1:Chiller Heater Heating Electric Power Unit 1 [W](Hourly) | 0.1 | 0.005 | 26 | 67.5% | 1584.2168
CHILLERHEATERMODULE 1:Chiller Heater Cooling Rate Unit 1 [W](Hourly) | 0.1 | 0.005 | 682 | 8.012% | 759.11
CHILLERHEATERMODULE 1:Chiller Heater Evaporator Inlet Temperature Unit 1 [C](Hourly) | 0.2 | -1 | 1078 | 14.55% | 1.8015
CHILLERHEATERMODULE 1:Chiller Heater Evaporator Outlet Temperature Unit 1 [C](Hourly) | 0.2 | -1 | 1016 | 11.9% | 0.69434
CHILLERHEATERMODULE 1:Chiller Heater Evaporator Mass Flow Rate Unit 1 [kg/s](Hourly) | 0.001 | 0.005 | 159 | 8.393% | 0.02648
CHILLERHEATERMODULE 1:Chiller Heater Condenser Heat Transfer Rate Unit 1 [W](Hourly) | 0.1 | 0.005 | 894 | 75.85% | 37.4045
CHILLERHEATERMODULE 1:Chiller Heater Capacity Temperature Modifier Multiplier Unit 1 [](Hourly) | 0.001 | 0.005 | 529 | 7.76% | 0.081853
CHILLERHEATERMODULE 1:Chiller Heater EIR Temperature Modifier Multiplier Unit 1 [](Hourly) | 0.001 | 0.005 | 537 | 7.597% | 0.063019
CHILLERHEATERMODULE 1:Chiller Heater EIR Part Load Modifier Multiplier Unit 1 [](Hourly) | 0.001 | 0.005 | 751 | 7.21% | 0.034629
CHILLERHEATERMODULE 1:Chiller Heater Condenser Inlet Temperature Unit 1 [C](Hourly) | 0.2 | -1 | 2842 | 121.1% | 12.8727
CHILLERHEATERMODULE 1:Chiller Heater Condenser Outlet Temperature Unit 1 [C](Hourly) | 0.2 | -1 | 2871 | 121.1% | 12.8727
CHILLERHEATERMODULE 1:Chiller Heater Operation Mode Unit 2 [](Hourly) | 0.001 | 0.005 | 12 | 20% | 0.5
CHILLERHEATERMODULE 1:Chiller Heater Part Load Ratio Unit 2 [](Hourly) | 0.001 | 0.005 | 973 | 21.76% | 0.13051
CHILLERHEATERMODULE 1:Chiller Heater Cycling Ratio Unit 2 [](Hourly) | 0.001 | 0.005 | 32 | 35.19% | 0.19976
CHILLERHEATERMODULE 1:Chiller Heater Cooling Electric Power Unit 2 [W](Hourly) | 0.1 | 0.005 | 757 | 18.55% | 698.5029
CHILLERHEATERMODULE 1:Chiller Heater Heating Electric Power Unit 2 [W](Hourly) | 0.1 | 0.005 | 201 | 32.53% | 2007.1942
CHILLERHEATERMODULE 1:Chiller Heater Cooling Rate Unit 2 [W](Hourly) | 0.1 | 0.005 | 903 | 26.6% | 1609.1674
CHILLERHEATERMODULE 1:Chiller Heater Evaporator Inlet Temperature Unit 2 [C](Hourly) | 0.2 | -1 | 1078 | 14.55% | 1.8015
CHILLERHEATERMODULE 1:Chiller Heater Evaporator Outlet Temperature Unit 2 [C](Hourly) | 0.2 | -1 | 1023 | 44.56% | 2.2282
CHILLERHEATERMODULE 1:Chiller Heater Evaporator Mass Flow Rate Unit 2 [kg/s](Hourly) | 0.001 | 0.005 | 197 | 66.66% | 0.11735
CHILLERHEATERMODULE 1:Chiller Heater Condenser Heat Transfer Rate Unit 2 [W](Hourly) | 0.1 | 0.005 | 938 | 75.85% | 37.4045
CHILLERHEATERMODULE 1:Chiller Heater Capacity Temperature Modifier Multiplier Unit 2 [](Hourly) | 0.001 | 0.005 | 538 | 7.76% | 0.081853
CHILLERHEATERMODULE 1:Chiller Heater EIR Temperature Modifier Multiplier Unit 2 [](Hourly) | 0.001 | 0.005 | 548 | 7.553% | 0.055664
CHILLERHEATERMODULE 1:Chiller Heater EIR Part Load Modifier Multiplier Unit 2 [](Hourly) | 0.001 | 0.005 | 954 | 26.05% | 0.13816
CHILLERHEATERMODULE 1:Chiller Heater Condenser Inlet Temperature Unit 2 [C](Hourly) | 0.2 | -1 | 2842 | 121.1% | 12.8727
CHILLERHEATERMODULE 1:Chiller Heater Condenser Outlet Temperature Unit 2 [C](Hourly) | 0.2 | -1 | 2881 | 121.1% | 12.8727
CHILLERHEATERMODULE 1:Chiller Heater Condenser Mass Flow Rate Unit 2 [kg/s](Hourly) | 0.001 | 0.005 | 21 | 33.97% | 0.083078
CHILLERHEATERMODULE 2:Chiller Heater Operation Mode Unit 3 [](Hourly) | 0.001 | 0.005 | 42 | 99900% | 0.5
CHILLERHEATERMODULE 2:Chiller Heater Part Load Ratio Unit 3 [](Hourly) | 0.001 | 0.005 | 460 | 99900% | 0.05
CHILLERHEATERMODULE 2:Chiller Heater Cycling Ratio Unit 3 [](Hourly) | 0.001 | 0.005 | 579 | 99900% | 0.0070514
CHILLERHEATERMODULE 2:Chiller Heater Cooling Electric Power Unit 3 [W](Hourly) | 0.1 | 0.005 | 673 | 20.16% | 285.9071
CHILLERHEATERMODULE 2:Chiller Heater Heating Electric Power Unit 3 [W](Hourly) | 0.1 | 0.005 | 50 | 99900% | 17.5262
CHILLERHEATERMODULE 2:Chiller Heater Cooling Rate Unit 3 [W](Hourly) | 0.1 | 0.005 | 516 | 99900% | 18.2619
CHILLERHEATERMODULE 2:Chiller Heater Evaporator Inlet Temperature Unit 3 [C](Hourly) | 0.2 | -1 | 1067 | 15.3% | 2.0223
CHILLERHEATERMODULE 2:Chiller Heater Evaporator Outlet Temperature Unit 3 [C](Hourly) | 0.2 | -1 | 1055 | 107.1% | 7.3235
CHILLERHEATERMODULE 2:Chiller Heater Evaporator Mass Flow Rate Unit 3 [kg/s](Hourly) | 0.001 | 0.005 | 726 | 277.8% | 0.21911
CHILLERHEATERMODULE 2:Chiller Heater Condenser Heat Transfer Rate Unit 3 [W](Hourly) | 0.1 | 0.005 | 577 | 99900% | 29.0996
CHILLERHEATERMODULE 2:Chiller Heater Capacity Temperature Modifier Multiplier Unit 3 [](Hourly) | 0.001 | 0.005 | 539 | 7.76% | 0.081853
CHILLERHEATERMODULE 2:Chiller Heater EIR Temperature Modifier Multiplier Unit 3 [](Hourly) | 0.001 | 0.005 | 493 | 8.789% | 0.062037
CHILLERHEATERMODULE 2:Chiller Heater EIR Part Load Modifier Multiplier Unit 3 [](Hourly) | 0.001 | 0.005 | 601 | 100.1% | 0.4382
CHILLERHEATERMODULE 2:Chiller Heater Condenser Inlet Temperature Unit 3 [C](Hourly) | 0.2 | -1 | 2842 | 121.1% | 12.8727
CHILLERHEATERMODULE 2:Chiller Heater Condenser Outlet Temperature Unit 3 [C](Hourly) | 0.2 | -1 | 2859 | 121.1% | 12.8727
CHILLERHEATERMODULE 2:Chiller Heater Condenser Mass Flow Rate Unit 3 [kg/s](Hourly) | 0.001 | 0.005 | 23 | 28.66% | 0.075708
CHILLERHEATERMODULE 2:Chiller Heater Operation Mode Unit 4 [](Hourly) | 0.001 | 0.005 | 161 | 99900% | 1.5
CHILLERHEATERMODULE 2:Chiller Heater Part Load Ratio Unit 4 [](Hourly) | 0.001 | 0.005 | 162 | 99900% | 0.15
CHILLERHEATERMODULE 2:Chiller Heater Cycling Ratio Unit 4 [](Hourly) | 0.001 | 0.005 | 162 | 99900% | 0.38613
CHILLERHEATERMODULE 2:Chiller Heater Cooling Electric Power Unit 4 [W](Hourly) | 0.1 | 0.005 | 1 | 23.95% | 3.5494
CHILLERHEATERMODULE 2:Chiller Heater Heating Electric Power Unit 4 [W](Hourly) | 0.1 | 0.005 | 162 | 99900% | 990.6336
CHILLERHEATERMODULE 2:Chiller Heater Cooling Rate Unit 4 [W](Hourly) | 0.1 | 0.005 | 162 | 99900% | 1000
CHILLERHEATERMODULE 2:Chiller Heater Evaporator Inlet Temperature Unit 4 [C](Hourly) | 0.2 | -1 | 1095 | 8.112% | 1.1875
CHILLERHEATERMODULE 2:Chiller Heater Evaporator Outlet Temperature Unit 4 [C](Hourly) | 0.2 | -1 | 1194 | 75.76% | 6.2371
CHILLERHEATERMODULE 2:Chiller Heater Evaporator Mass Flow Rate Unit 4 [kg/s](Hourly) | 0.001 | 0.005 | 163 | 188.3% | 0.19747
CHILLERHEATERMODULE 2:Chiller Heater Condenser Heat Transfer Rate Unit 4 [W](Hourly) | 0.1 | 0.005 | 213 | 99900% | 1116.4507
CHILLERHEATERMODULE 2:Chiller Heater Capacity Temperature Modifier Multiplier Unit 4 [](Hourly) | 0.001 | 0.005 | 11 | 3.131% | 0.035566
CHILLERHEATERMODULE 2:Chiller Heater EIR Temperature Modifier Multiplier Unit 4 [](Hourly) | 0.001 | 0.005 | 36 | 8.789% | 0.062037
CHILLERHEATERMODULE 2:Chiller Heater EIR Part Load Modifier Multiplier Unit 4 [](Hourly) | 0.001 | 0.005 | 200 | 68.77% | 0.37193
CHILLERHEATERMODULE 2:Chiller Heater Condenser Inlet Temperature Unit 4 [C](Hourly) | 0.2 | -1 | 2842 | 121.1% | 12.8727
CHILLERHEATERMODULE 2:Chiller Heater Condenser Outlet Temperature Unit 4 [C](Hourly) | 0.2 | -1 | 2846 | 121.1% | 12.8727
CHILLERHEATERMODULE 2:Chiller Heater Condenser Mass Flow Rate Unit 4 [kg/s](Hourly) | 0.001 | 0.005 | 17 | 83.46% | 0.15125
ShopWithPVandBattery | [5 empty] | Existing warnings
KIBAM:Electric Storage Degradation Fraction [](Hourly) | 0.001 | 0.005 | 1 | 0.809% | 0.00091955
FourPipeBeamLargeOffice | [5 empty] | Diffs in existing warnings
COOLSYS1 CHILLER 1:Chiller Electric Power [W](Hourly) | 0.1 | 0.005 | 2 | 11.47% | 32.5511 | ************* ** Warning ** CoolingTower:SingleSpeed "TOWERWATERSYS COOLTOWER" Cooling tower water outlet temperature is below the specified minimum condenser loop temp error continues...
COOLSYS1 CHILLER 1:Chiller Evaporator Mass Flow Rate [kg/s](Hourly) | 0.001 | 0.005 | 1 | 10.22% | 1.0935 | - ************* ** ~~~ ** This error occurred 1047 total times;
+ ************* ** ~~~ ** This error occurred 1137 total times;
5ZoneAirCooledDemandLimiting_FixedRateVentilation | [5 empty] | Existing warnings
HW CIRC PUMP:Pump Electric Power [W](Hourly) | 0.1 | 0.005 | 2 | 5.434% | 1.4956